## Sheet1
Project: | P234 - Maintenance Hangar |  |  |  | USER NOTES (Not intended to print)
Location: | Anytown, VA
Project #: | 12345678
Date: | 2017-04-10
STATEMENT OF SPECIAL INSPECTIONS (01 45 35-A) |  |  |  |  | < Edit Blue text/cells only
Project Seismic Design Category: |  | E |  |  | SPECIAL INSPECTOR OF RECORD (SIOR) DETERMINATION |  | A | I | Yes
Project Risk Category: |  | IV |  |  |  |  | B | II | No
Project Design Wind Speed (km/h): |  | 392 |  |  | < The Special Inspector of Record (SIOR) is a DOD mandate. Enter the requested data to determine whether an SIOR is required or is not required. |  | C | III
Number of Stories: |  | 2 |  |  |  |  | D | IV
Structure Height Above Grade (M): |  | 21 |  |  |  |  | E | V
Hazardous Occupancy or attached to such? |  | No | Group H Occupancies (2018 IBC, Section 415) |  |  |  | F
Special Inspector of Record (SIOR)
A Special Inspector of Record (SIOR) |  | IS |  | required (per UFGS 01 45 35, Section 1.3.8)
SIOR Name (Registered Professional): |  | John Doe P.E. |  |  | < For DB contracts insert the SIOR contact information. For DBB contracts enter, "Contractor to provide prior to construction start".
Professional Registration Number: |  | C222222
Consulting Firm Name (if any): |  | ABC Structural Consulting |  |  | < The SIOR must be a registered professional engineer, and must not be an employee of the General Contractor, or an employee of a Sub-Contractor performing construction for this project.
SIOR Office AND Mobile Phone Number: |  | 1234567895 (Mobile), 123456789 (Office)
This Statement of Special Inspections is in accordance with Section 1704.3 of the 2018 IBC. It includes a Schedule of Special Inspections applicable to the above referenced project. |  |  |  |  | LATERAL FORCE RESISTING SYSTEM IDENTIFICATION
2018 IBC 1704.3.2 and 1704.3.3
Following is a listing of critical main wind/seismic force resisting systems for this structure. Carefully inspect these elements as part of the roles and responsibilities of the Special Inspector (reference the Schedule of Special Inspections for inspection checklists).
Vertical LFRS Elements |  |  |  | Notes
Ordinary Concentric Braced Frames |  |  |  | North - South Direction Only, See Plan
Special Concentric Braced Frames |  |  |  | Lettered Gridline only, see plan for call out
Ordinary Steel Moment resisting Frames (SMRF) |  |  |  | Both orthogonal Directions, See plan for call out
Ordinary Reinforced Concrete Shearwalls |  |  |  | See Key Notes
Concrete Grade Beams Resisting Lateral Loads |  |  |  | Office Portion Only, see plan key notes
Ordinary Reinforced Masonry Shear Walls |  |  |  | High Bay, Numbered Gridlines only, see plan
OSB Sheathed Shear Walls (nailing, sill bolting, Etc) |  |  |  | See schedule on plan
Shear Wall Hold Downs |  |  |  | Identified on Plan & in Detail Sheet X.XX
Horizontal LFRS Elements |  |  |  | Notes
Continuous Roof Ties |  |  |  | See Key Notes on Roof Plan
Collector Elements |  |  |  | Identified on plan with key notes
Concrete over metal deck |  |  |  | 2nd floor and roof
Metal Roof Deck & Related Fastening System |  |  |  | See Roof Plan
Out of Plane Wall Connections |  |  |  | See Structural Details XX & XX
Diaphragm Cross Rod Bracing |  |  |  | See Roof Plan for locations
Cast in Place Concrete Floor and Roof Diaphragms |  |  |  | See sheet XX for details and rebar schedule
Special Force Transfer Connection |  |  |  | See Detail X on Sheet X.XX
Statement of Special Inspections Page 1 of 2 Japan Edited Specifications, Feb 2020
Project: | P234 - Maintenance Hangar |  |  |  | DESIGNATED SEISMIC SYSTEMS (DSS)
Location: | Anytown, VA |  |  |  | This section identifies whether Designated Seismic Systems apply to this project or do not apply. Additionally, and where DSS apply, some explanation is provided below for what a Designated Seismic System is for this specific project.
Project #: | 12345678
Date: | 2017-04-10
Designated Seismic Systems (DSS)
(2018 IBC 1705.13.3.4) (ASCE 7-16, 13.2.2, C13.2.2) (UFC 3-301-04, 2-11.2 & 2-13.2.2)
Non-structural 'Designated Seismic Systems' (DSS) have an Ip greater than 1.0, and must be certified by the manufacturer to remain operable after a design earthquake. The Prime Contractor shall collect the manufacturers Certificates of Compliance for incorporation into the Operations and Maintenance manual per Section 01 78 23 paragraph 1.3. The SIOR shall review the Certificates of Compliance as part of the special inspection. Additionally, the below listed Designated Seismic Systems must be carefully inspected by the Special Inspector according to the requirements noted in the Schedule of Special Inspections. |  |  |  |  | < Designated Seismic Systems APPLY to this project. List all Designated Seismic Systems in the blue tables below. Some DSS suggestions are already populated, delete or keep as necessary.
ELECTRICAL Designated Seismic Systems (DSS) Requiring a Certificate of Compliance | [5 empty] | DSS for this project are nonstructural components with an importance factor of 1.5 AND with the following project conditions (UFC 3-301 SECTION 2-11.2) (ASCE 7-16, 13.1.3):
1. | DSS Emergency or Standby Power System
2. | DSS Lighting Inverters and Associated Conduits
3. | DSS Electrical System (including conduits) and Panels Serving Fire Pump Controller and Fire Pump |  |  |  |  | 1. The component is required to function for life-safety purposes after an earthquake, including fire sprinkler systems and egress stairways (RC I thru V + SDC C thru F).
4. | DSS Light Fixture with Emergency Battery Backup
5. | DSS Component XX
If additional space is required, append an additional sheet listing the remaining DSS | [5 empty] | 2. The component conveys, supports, or otherwise contains toxic, highly toxic, or explosive substances where the quantity of the a material exceeds a threshold quantity established by the authority having jurisdiction and is sufficient to pose a threat to the public if released (RC I thru V + SDC C thru F).
MECHANICAL/PLUMBING Designated Seismic Systems (DSS) Requiring a Certificate of Compliance
1. | DSS Gas lines and associated fittings, anchorage, & flexible Connections
2. | DSS Component XX
3. | DSS Component XX
4. | DSS Component XX |  |  |  |  | 3. The component is in, or attached to, a Risk Category IV or V structure, and it is needed for continued operation of the facility, or its faiure could impair the continued operation of the facility (RC IV thru V + SDC C thru F).
5. | DSS Component XX
If additional space is required, append an additional sheet listing the remaining DSS
OTHER Designated Seismic Systems (DSS) Requiring a Certificate of Compliance | [5 empty] | 4. The component conveys, supports, or otherwise contains hazardous substances and is attached to a structure, or portion thereof, classified by the authority having jurisdiction as a hazardous occupancy (RC I thru V + SDC C thru F).
1. | DSS Building egress stair systems
2. | DSS Building fire sprinkler systems
3. | DSS Elevator System, see specification section 14 21 23
4. | DSS Fire pump, Fire pump controller, fire alarm control panel and mass notification
5. | DSS Component XX
Final Walk Down Inspection and Report |  |  |  |  | FINAL WALK DOWN INSPECTION AND REPORT FOR NON-STRUCTURAL DSS
(UFC 3-301-01 SECTION 2-2.4.3)
Designated Seismic Systems shall receive a final walk-down inspection by the Registered Design Professional in Responsible Charge. |  |  |  |  | < A non-structural DSS final walk down inspection applies to this project
Final Walk Down Report, Prepared by the Registered Design Professional in Responsible Charge, Must Include:
1. Record observations of Final Walk Down Inspection
2. Document that Inspections were performed in accordance with the Schedule of Special Inspections |  |  |  |  | < …Certificates of compliance documenting that the requirements are met shall be submitted to the building official (2018 IBC 1704.5 & 1705.13.3) and shall be maintained in a file identified as "Equipment Certification Documentation". This file shall be part of the final project O&M Manual
3. Document that all Designated Seismic Systems are installed according to construction/manufacturer document requirements, and that Compliance Certificates have been collected (UFC 3- 301-01, 01, 2-13.2.2.1).
Statement of Special Inspections Page 2 of 2 Japan Edited Specifications, Feb 2020
NEXT: COMPLETE THE SCHEDULE OF SPECIAL INSPECTIONS TEMPLATE.
Edit, print, and append the Schedule of Special Inspections Template to this Statement of Special Inspections and insert both at the back of the project Special Inspections Specification (01 45 35).
Request Schedule of Special Inspection Template from USACE for Japan Projects.
Note on B5: Can be a contract and task order number or other identifiying database identification number such as an Eprojects # (navy)